## Word Mapping
Data Protocol Mapping for ESEPRO GCP-30/MFR 3 Emulation using Easygen-3000XT
Version 4, 13/2/2024
No. | Profibus | GCP-30 Content | MFR 3 Content | GCP-30 Unit | Easygen-3000XT Start addr. | Type | Easygen Description | EG Unit | Conversion Operation | Comment
1 | 10 | Generator voltage delta V12 | Protocol number | V x 10^gen_volt_exp | GCP-30: 50073 | int32 | Gen. voltage L1-L2 | 0.1 V | divide by 10 | MFR 3: Protocol number 1300
2 | 12 | Generator frequency f | Generator frequency f | Hz x 100 | 50006 | int16 | Gen. frequency | 0.01 Hz | 1:1
3 | 14 | Actual generator real power P | Actual generator real power P | W × 10^PGNEXPO | 50052 | int32 | Total gen. power | 1 W | divide by 1000
4 | 16 | Generator kW and V exponent | Generator kW and V exponent | - | - | - | n/a | - | set to 3 for kW, set to 0 for V
5 | 18 | Real power set point value | Real power set point value | kW * PGNWD/2800 | 50130 | int32 | Setpoint active power | 0.1 kW | divide by 10
6 | 20 | Conversion factor steps to kW | Conversion factor steps to kW | - | - | - | n/a | - | set to 2800
7 | 22 | Bus bar voltage delta V12 | Bus bar voltage delta V12 | V x 10^bus_volt_exp | 50016 | int32 | Average Mains Delta-Volt | 0.1 V | divide by 10
8 | 24 | Mains voltage delta V12 | Mains voltage delta V12 | V x 10^main_volt_exp | 50091 | int32 | Mains voltage L1-L2 | 0.1 V | divide by 10
9 | 26 | Currently present alarm class | Currently present alarm class | register | 50105 | uint16 | Class A, B, C, D, E, F | - | map bits | Refer to Register Bits mapping sheet
10 | 28 | Control Register 2 GCP-30 | Control Register 2 MFR-3 | register | 50018, 50137, 50139 | uint16 |  | - | map bits | Refer to Register Bits mapping sheet
11 | 30 | Mains interchange (import/export) real power | Mains interchange (import/export) real power | x10^main_kw_exp | 50055 | int32 | External total mains power | W | divide by 1000
12 | 32 | Control Register 1 | internal |  | GCP-30: 50018, 50186 | uint16 |  | - | map bits | GCP-30: Refer to Register Bits mapping sheet, MFR 3: set to 0
13 | 34 | Alarm message IKD (SC06) | Alarms 8 |  | 50090 | uint16 |  | - | map bits | Refer to Register Bits mapping sheet
14 | 36 | Internal alarm 6 | Internal alarms 6 |  | 50063, 50066, 50108 | uint16 |  | - | map bits | Refer to Register Bits mapping sheet
15 | 38 | Generator voltage delta V23 | Generator voltage delta V23 | V x 10^gen_volt_exp | 50079 | int32 | Gen. voltage L2-L3 | 0.1 V | divide by 10
16 | 40 | Generator voltage delta V31 | Generator voltage delta V31 | V x 10^gen_volt_exp | 50085 | int32 | Gen. voltage L3-L1 | 0.1 V | divide by 10
17 | 42 | Generator voltage delta V1N | Generator voltage delta V1N | V x 10^gen_volt_exp | 50076 | int32 | Gen. voltage L1-N | 0.1 V | divide by 10
18 | 44 | Generator voltage delta V2N | Generator voltage delta V2N | V x 10^gen_volt_exp | 50082 | int32 | Gen. voltage L2-N | 0.1 V | divide by 10
19 | 46 | Generator voltage delta V3N | Generator voltage delta V3N | V x 10^gen_volt_exp | 50088 | int32 | Gen. voltage L3-N | 0.1 V | divide by 10
20 | 48 | Configuration [T1]-[T4] | Generator voltage delta V12 | V x 10^gen_volt_exp | MFR 3: 50073 | int32 | Gen. voltage L1-L2 | 0.1 V | divide by 10 | GCP-30: set to 0
21 | 50 | Engine speed measured via the Pickup | internal | 1min | 50001 | int16 | Pickup speed | 1 rpm | 1:1
22 | 52 | Generator current in L1 | Generator current in L1 | A | 50034 | int32 | Gen. current 1 | 0.001 A | divide by 1000
23 | 54 | Generator current in L2 | Generator current in L2 | A | 50037 | int32 | Gen. current 2 | 0.001 A | divide by 1000
24 | 56 | Generator current in L3 | Generator current in L3 | A | 50040 | int32 | Gen. current 3 | 0.001 A | divide by 1000
25 | 58 | Actual generator reactive power | Actual generator reactive power | var × 10^PGNEXPO | 50058 | int32 | Total gen. reactive power | 1 var | divide by 1000
26 | 60 | Generator cos phi | Generator cos phi | x 100 | 50003 | int16 | Gen. Power factor | 0.001 | divide by 10
27 | 62 | Current reserve power in the system in kW | internal | kW | 50172 | int32 | Active power reserve in system (in own segment) | kW | 1:1
28 | 64 | Current actual real power in the system | internal | kW | 50169 | int32 | Active real power in system | kW | 1:1
29 | 66 | Number of participants on the CAN bus | Number of participants on the CAN bus |  | - |  |  | - | set to 0
30 | 68 | High byte: Mains status, Low byte: Generator status | High byte: Mains status, Low byte: Generator status | register | 50186 | uint16 |  | - | map bits | Mains status: 02.11 Mains voltage and frequency in range, Generator status: 02.03 Generator voltage in range
31 | 70 | Generator Current Exponent | Generator Current Exponent | - | - | - | n/a | - | set to 0 for A
32 | 72 | Bus bar frequency | Bus bar frequency | Hz x 100 | 50015 | int32 | Busbar Frequency | 0.01 Hz | 1:1
33 | 74 | Configuration [T5]-[T8] | Busbar status |  | MFR 3: 50186 | uint16 |  | - | map bits | GCP-30: set to 0, MFR 3: 02.06 Busbar voltage in range
34 | 76 | Mains voltage delta V23 | Mains voltage delta V23 | V x 10^main_volt_exp | 50097 | int32 | Mains voltage L2-L3 | 0.1 V | divide by 10
35 | 78 | Mains voltage delta V31 | Mains voltage delta V31 | V x 10^main_volt_exp | 50103 | int32 | Mains voltage L3-L1 | 0.1 V | divide by 10
36 | 80 | Mains voltage delta V1N | Mains voltage delta V1N | V x 10^main_volt_exp | 50094 | int32 | Mains voltage L1-N | 0.1 V | divide by 10
37 | 82 | Mains voltage delta V2N | Mains voltage delta V2N | V x 10^main_volt_exp | 50100 | int32 | Mains voltage L2-N | 0.1 V | divide by 10
38 | 84 | Mains voltage delta V3N | Mains voltage delta V3N | V x 10^main_volt_exp | 50106 | int32 | Mains voltage L3-N | 0.1 V | divide by 10
39 | 86 | Mains frequency out off VN12/VN23/VN31 | Mains frequency out off VN12/VN23/VN31 | Hz x 100 | 50009 | int32 | Mains frequency | 0.01 Hz | 1:1
40 | 88 | Mains current in L1 | Mains current in L1 | x10^main_amp_exp | 50043 | int32 | Mains current L1 | 0.001 A | divide by 1000
41 | 90 | Mains reactive power | Mains reactive power | x10^main_kw_exp | 50061 | int32 | External total mains reactive power | 1 var | divide by 1000
42 | 92 | Mains power factor | Mains power factor | x 100 | 50012 | int16 | Mains power factor | 0.001 | divide by 10
43 | 94 | Mains power and voltage exponents | Mains power and voltage exponents | - | - | - | n/a | - | set to 3 for kW, set to 0 for V
44 | 96 | Mains current and bus voltage exponents | Mains current and bus voltage exponents | - | - | - | n/a | - | set to 0 for V, set to 0 for A
45 | 98 | Engine operating hours, high word | Engine operating hours, high word | h x 32767 | 50127 | uint32 | Gen. hours of operation | 0.01 h | divide by 100
46 | 100 | Engine operating hours, low word | Engine operating hours, low word | h | 50127 | uint32 | Gen. hours of operation | 0.01 h | divide by 100
47 | 102 | Hours until next maintenance | Hours until next maintenance | h | 50126 | int16 | Hours until next maintenance | 1 h | 1:1
48 | 104 | Engine start number | Engine start number | - | 50123 | uint16 | Engine, number of start requests | - | 1:1
49 | 106 | Operation mode | Internal |  | 50002 | uint16 |  | - | map bits | Refer to Register Bits mapping sheet
50 | 108 | Generator active energy, high word | Generator active energy, high word | kWh x 32767 | 50121 | uint32 | Gen. real energy | 0.01 MWh | multiply by 10
51 | 110 | Generator active energy, low word | Generator active energy, low word | kWh | 50121 | uint32 | Gen. real energy | 0.01 MWh | multiply by 10
52 | 112 | Battery voltage | Battery voltage | V x 10 | 50021 | int16 | Battery voltage | 0.1 V | 1:1
53 | 114 | Internal alarm 1 | Internal alarms 1 | register | 50072, 50075, 50102 | uint16 |  | - | map bits | Refer to Register Bits mapping sheet
54 | 116 | Internal alarm 2 | Internal alarms 2 | register | 50075, 50078 | uint16 |  | - | map bits | Refer to Register Bits mapping sheet
55 | 118 | Internal alarm 3 | Internal alarms 3 | register | 50018, 50063, 50066, 50072, 50075 | uint16 |  | - | map bits | Refer to Register Bits mapping sheet
56 | 120 | Internal alarm 4 | Internal | register | 50216 | uint16 |  | - | map bits | Refer to Register Bits mapping sheet
57 | 122 | Internal alarm 5 | Internal | register | 50216 | uint16 |  | - | map bits | Refer to Register Bits mapping sheet
58 | 124 | External alarm 1 | External alarms 1 | register | 50090 | uint16 |  | - | map bits | Refer to Register Bits mapping sheet
59 | 126 | External alarm 2 | External alarms 2 | register | 50090 | uint16 |  | - | map bits | Refer to Register Bits mapping sheet
60 | 128 | Internal alarm 7 | Internal alarms 7 | register | 50063 | uint16 |  | - | map bits | Refer to Register Bits mapping sheet
61 | 130 | Analogue input T1 | Analogue input T1 | use analogue manager | 50142 | uint16 | External Analog input 1 | - | 1:1
62 | 132 | Analogue input T2 | Analogue input T2 | use analogue manager | 50143 | uint16 | External Analog input 2 | - | 1:1
63 | 134 | Analogue input T3 | Analogue input T3 | use analogue manager | 50144 | uint16 | External Analog input 3 | - | 1:1
64 | 136 | Analogue input T4 | Analogue input T4 | use analogue manager | 50145 | uint16 | External Analog input 4 | - | 1:1
65 | 138 | Analogue input T5 | Analogue input T5 | use analogue manager | 50146 | uint16 | External Analog input 5 | - | 1:1
66 | 140 | Analogue input T6 | Analogue input T6 | use analogue manager | 50147 | uint16 | External Analog input 6 | - | 1:1
67 | 142 | Analogue input T7 | Analogue input T7 | use analogue manager | 50148 | uint16 | External Analog input 7 | - | 1:1
68 | 144 | Alarm messages IKD2 (SC06) | Internal | register | 50090 | uint16 |  | - | map bits | Refer to Register Bits mapping sheet
69 high byte | 145 | LCD-display | Internal |  | - | uint8 |  | - | set to 255 | No message to display, not supported
69 low byte | 146 | Pickup | Speed detection |  | 50018 | uint8 |  | - | map bits | 96.16 Internal Flag 16 = Machine is running, 96.15 Internal Flag 15 = Firing speed reached

## Register Bits mapping
Register Bits Mapping for ESEPRO GW-4 to GCP-30/MFR 3 Emulation using Easygen-3000XT
Version 4, 13/2/2024
GCP-30 / MFR 3 Register Name | Mux No. | Easygen-3000XT Register Name | Comment
Currently present alarm class
Alarm class F2 or alarm class F3 | 9 | Class C, D, E, F
LED "Alarm" flashes | 9 | 01.11 New Alarm triggered
Alarm class F3 | 9 | Class E, F
Alarm class F2 | 9 | Class C, D
Alarm class F1 | 9 | Class B
Alarm class F0 | 9 | Class A
Control Register 1 (GCP-30 only)
Starting enabled | 12 | 96.01 Internal flag 1
Execution of acknowledgment of a class F2/F3 alarm | 12 | n/a
Execution of acknowledgment of a class F1 alarm | 12 | n/a
State of generator busbar 1 = OK | 12 | 02.06 Busbar voltage in range
Control Register 2
Terminal 3 is energized | 10 | 96.02 Internal flag 2
Terminal 5 is energized | 10 | 96.03 Internal flag 3
Terminal 53 is energized, DI "Enable MCB" | 10 | 86.85 LM Enable MCB
Terminal 4, reply: GCB is closed | 10 | 04.06 GCB is closed
Terminal 54, reply: MCB is closed | 10 | 04.07 MCB is closed
Terminal 6 is energized | 10 | 96.04 Internal Flag 4
Shutdown power reached (GCP-30) | 10 | 96.05 Internal Flag 5
Alarm message IKD (GCP-30 only)
Failure DI8 of the IKD1.1 | 13 | 12.01 External discrete input 8 latched
Failure DI7 of the IKD1.1 | 13 | 12.01 External discrete input 7 latched
Failure DI6 of the IKD1.1 | 13 | 12.01 External discrete input 6 latched
Failure DI5 of the IKD1.1 | 13 | 12.01 External discrete input 5 latched
Failure DI4 of the IKD1.1 | 13 | 12.01 External discrete input 4 latched
Failure DI3 of the IKD1.1 | 13 | 12.01 External discrete input 3 latched
Failure DI2 of the IKD1.1 | 13 | 12.01 External discrete input 2 latched
Failure DI1 of the IKD1.1 | 13 | 12.01 External discrete input 1 latched
Internal alarm 6
MPU plausibility fault (GCP-30) | 14 | 08.48 MCB plausibility
Engine shutdown malfunction (GCP-30) | 14 | 05.06 LM Shutdown malfunction detected latched
Time overrun, GCB dead bus switching | 14 | 08.05 LM GCB fail to close latched
MCB open switch malfunction | 14 | 08.08 LM MCB fail to open latched
GCB open switch malfunction | 14 | 08.06 LM GCB fail to open latched
MCB synchronization time monitoring | 14 | 08.31 Timeout Synchronisation MCB latched
GCB synchronization time monitoring | 14 | 08.30 Timeout Synchronisation GCB latched
Range alarm analog input [T8] (GCP-30) | 14 | 10.08 Analog input 8 wire break
Range alarm analog input [T7] (GCP-30) | 14 | 10.07 Analog input 7 wire break
Range alarm analog input [T6] (GCP-30) | 14 | 10.06 Analog input 6 wire break
Range alarm analog input [T5] (GCP-30) | 14 | 10.05 Analog input 5 wire break
Range alarm analog input [T4] (GCP-30) | 14 | 10.04 Analog input 4 wire break
Range alarm analog input [T3] (GCP-30) | 14 | 10.03 Analog input 3 wire break
Range alarm analog input [T2] (GCP-30) | 14 | 10.02 Analog input 2 wire break
Range alarm analog input [T1] | 14 | 10.01 Analog input 1 wire break
Operation mode (GCP-30 only)
LOAD TEST operation mode | 49 | 96.06 Internal Flag 6
STOP operation mode | 49 | Control mode (STOP/AUTO/MANUAL/TEST)
TEST operation mode | 49 | Control mode (STOP/AUTO/MANUAL/TEST)
MANUAL operation mode | 49 | Control mode (STOP/AUTO/MANUAL/TEST)
AUTOMATIC operation mode | 49 | Control mode (STOP/AUTO/MANUAL/TEST)
Emergency power is ON | 49 | 04.09 Emergency mode is currently active
Emergency power is OFF | 49 | inverse of 04.09 Emergency mode is currently active
Delayed engine monitoring is ON | 49 | 03.07 Engine monitoring delay expired
Cool down expired | 49 | 96.07 Internal Flag 7
Internal alarm 1
F3: Generator overfrequency 1 | 53 | 06.01 Generator over frequency 1 latched
F3: Generator underfrequency 1 | 53 | 06.03 Generator under frequency
F3: Generator overvoltage 1 | 53 | 06.05 Generator over voltage 1 latched
F3: Generator undervoltage 1 | 53 | 06.07 Generator under voltage 1 latched
F1: Battery undervoltage | 53 | 08.04 Battery under voltage 2 latched OR 08.03 Battery under voltage 1 latched
F3: Generator overload | 53 | 06.14 Generator overload IOP 1 latched OR 06.15 Generator overload IOP 2 latched OR 06.23 Generator overload MOP 1 latchedd OR 06.24 Generator overload MOP 2 latched
F3: Generator reverse power | 53 | 06.12 Reverse / reduced power 1 latched OR 06.13 Reverse / reduced power 2 latched
Internal alarm 2
F0: Mains overfrequency | 54 | 07.06 Mains over frequency 1 latched OR 07.07 Mains over frequency 2 latched
F0: Mains underfrequency | 54 | 07.08 Mains under frequency 1 latched OR 07.09 Mains under frequency 2 latched
F0: Mains overvoltage | 54 | 07.10 Mains over voltage 1 latched OR 07.11 Mains over voltage 2 latched
F0: Mains undervoltage | 54 | 07.12 Mains under voltage 1 latched OR 07.13 Mains under voltage 2 latched
Interface fault X1-X5 | 54 | n/a
GCB opened; "Time add-on ramp" expired | 54 | 06.30 Generator unloading mismatch Latched
F0: df/dt fault | 54 | 07.15 Mains df/dt latched
F0: Mains phase/vector jump | 54 | 07.14 Mains Phase shift latched
Internal alarm 3
F3: Time-overcurrent, level 2 | 55 | 06.10 Generator over current 2 latched OR 06.11 Generator over current 3 latched
F3: Generator overspeed (Pickup) | 55 | 05.01 LM Engine Over speed 1 latched OR 05.02 LM Engine Over speed 2 latched
Import power 0 kW not reached | 55 | 96.08 Internal Flag 8
F3: Generator unbalanced load | 55 | 06.16 Generator unbalanced load 1 latched OR 06.17 Generator unbalanced load 2 latched
F3: Time-overcurrent, level 1 | 55 | 06.09 Generator over current 1 latched
Interface fault Y1-Y5 | 55 | 08.19 CANopen error at CAN Interface 2 (ECU)
F1: Maintenance call | 55 | 05.09 LM Maintenance days exceeded latched OR 05.10 LM Maintenance hours exceeded latched
Start failure | 55 | 05.08 LM Start fail detected latched
Internal alarm 4
F1: Analog input [T1], level 1 | 56 | 16.01 Free alarm 1 latched
F3: Analog input [T1], level 2 | 56 | 16.02 Free alarm 2 latched
F1: Analog input [T2], level 1 | 56 | 16.03 Free alarm 3 latched
F3: Analog input [T2], level 2 | 56 | 16.04 Free alarm 4 latched
F1: Analog input [T3], level 1 | 56 | 16.05 Free alarm 5 latched
F3: Analog input [T3], level 2 | 56 | 16.06 Free alarm 6 latched
F1: Analog input [T4], level 1 | 56 | 16.07 Free alarm 7 latched
F3: Analog input [T4], level 2 | 56 | 16.08 Free alarm 8 latched
Internal alarm 5
F1: Analog input [T5], level 1 | 57 | 16.09 Free alarm 9 latched
F3: Analog input [T5], level 2 | 57 | 16.10 Free alarm 10 latched
F1: Analog input [T6], level 1 | 57 | 16.11 Free alarm 11 latched
F3: Analog input [T6], level 2 | 57 | 16.12 Free alarm 12 latched
F1: Analog input [T7], level 1 | 57 | 16.13 Free alarm 13 latched
F3: Analog input [T7], level 2 | 57 | 16.14 Free alarm 14 latched
External alarm 1 and 2
Discrete input [D01] | 58 | 09.01 Discrete input 1 latched
Discrete input [D02] | 58 | 09.02 Discrete input 2 latched
Discrete input [D03] | 58 | 09.03 Discrete input 3 latched
Discrete input [D04] | 58 | 09.04 Discrete input 4 latched
Discrete input [D05] | 58/59 | 09.05 Discrete input 5 latched
Discrete input [D06] | 58/59 | 09.06 Discrete input 6 latched
Discrete input [D07] | 58/59 | 09.07 Discrete input 7 latched
Discrete input [D08] | 58/59 | 09.08 Discrete input 8 latched
Discrete input [D09] | 59 | 09.09 Discrete input 9 latched
Discrete input [D10] | 59 | 09.10 Discrete input 10 latched
Discrete input [D11] | 59 | 09.11 Discrete input 11 latched
Discrete input [D12] | 59 | 09.12 Discrete input 12 latched
GCP-30 Discrete input [D13], MFR3 Terminal 34 | 58/59 | 09.13 Discrete input 13 latched
GCP-30 Discrete input [D14], MFR3 Terminal 35 | 58/59 | 09.14 Discrete input 14 latched
GCP-30 Discrete input [D15], MFR3 Terminal 36 | 58/59 | 09.15 Discrete input 15 latched
GCP-30 Discrete input [D16], MFR3 Terminal 61 | 58/59 | 09.16 Discrete input 16 latched
Internal alarm 7
MCB close malfunction | 60 | 08.07 LM MCB fail to close latched
GCB close malfunction | 60 | 08.05 LM GCB fail to close latched
Immediate stop | 60 | 05.05 LM Unintended stop detected latched
F3: inverse-time over current time protection (MFR3) | 25 | 06.22 Inverse time over current Latched
F3: ground current failure (MFR3) | 25 | 06.19 Ground fault 1 latched OR 06.20 Ground fault 2 latched
Alarm messages IKD2 (SC10)
Failure DI8 of the IKD1.2 | 68 | 12.01 External discrete input 16 latched
Failure DI7 of the IKD1.2 | 68 | 12.01 External discrete input 15 latched
Failure DI6 of the IKD1.2 | 68 | 12.01 External discrete input 14 latched
Failure DI5 of the IKD1.2 | 68 | 12.01 External discrete input 13 latched
Failure DI4 of the IKD1.2 | 68 | 12.01 External discrete input 12 latched
Failure DI3 of the IKD1.2 | 68 | 12.01 External discrete input 11 latched
Failure DI2 of the IKD1.2 | 68 | 12.01 External discrete input 10 latched
Failure DI1 of the IKD1.2 | 68 | 12.01 External discrete input 9 latched
Alarms 8 (MFR 3 only)
F3: Generator overfrequency, level 2 | 13 | 06.02 Generator over frequency 2 latched
F3: Generator underfrequency, level 2 | 13 | 06.04 Generator under frequency 2 latched
F3: Generator overvoltage, level 2 | 13 | 06.06 Generator over voltage 2 latched
F3: Generator undervoltage, level 2 | 13 | 06.08 Generator under voltage 2 latched
F3: Reactive power, inductive | 13 | 16.15 Free alarm 15 latched
F3: Reactive power, capacitive | 13 | 16.16 Free alarm 16 latched