## Word Mapping
Data Protocol Mapping for ESEPRO MFR 2 Emulation using Easygen-3000XT
Version 3, 29/08/2024
Profibus Word | Content | Unit | 5014 Mux | Easygen-3000XT Start addr. | Type | Easygen Description | Unit | Conversion Operation | Comment
0 | Telegram call sign | "409" | n/a | n/a | int16 | n/a | - | Emulated
1 | Generator voltage L12 | V | 24 | 50073 | int32 | Gen. voltage L1-L2 | 0.1 V | divide by 10
2 | Generator voltage L23 | V | 26 | 50079 | int32 | Gen. voltage L2-L3 | 0.1 V | divide by 10
3 | Generator voltage L31 | V | 28 | 50085 | int32 | Gen. voltage L3-L1 | 0.1 V | divide by 10
4 | Generator frequency | Hz x 10 | 2 | 50006 | int16 | Gen. frequency | 0.01 Hz | divide by 10
5 | Generator current L1 | A | 11 | 50034 | int32 | Gen. current 1 | 0.001 A | divide by 1000
6 | Generator current L2 | A | 12 | 50037 | int32 | Gen. current 2 | 0.001 A | divide by 1000
7 | Generator current L3 | A | 13 | 50040 | int32 | Gen. current 3 | 0.001 A | divide by 1000
8 | Generator power factor | - | 1 | 50003 | int16 | Gen. Power factor | 0.001 | divide by 10
9 | Generator real power | kW | 17 | 50052 | int32 | Total gen. power | W | divide by 1000
10 | Engine speed (optionally) | 1min | 0 | 50001 | int16 | Pickup speed | 1 rpm | 1:1
11 | Busbar voltage | V | 5 | 50016 | int32 | Average Mains Delta-Volt | 0.1 V | divide by 10
12 | Busbar frequency | Hz x 10 | 5 | 50015 | int16 | Busbar Frequency | 0.01 Hz | divide by 10
13 | Mains voltage L12 | V | 30 | 50091 | int32 | Mains voltage L1-L2 | 0.1 V | divide by 10
14 | Mains voltage L23 | V | 32 | 50097 | int32 | Mains voltage L2-L3 | 0.1 V | divide by 10
15 | Mains voltage L31 | V | 34 | 50103 | int32 | Mains voltage L3-L1 | 0.1 V | divide by 10
16 | Mains frequency | Hz x 10 | 3 | 50009 | int16 | Mains frequency | 0.01 Hz | divide by 10
17 | Mains current L1 | A | 14 | 50043 | int32 | Mains current L1 | 0.001 A | divide by 1000
18 | Mains power factor | - | 4 | 50012 | int16 | Mains power factor | 0.001 | divide by 10
19 | Mains interchange real power | kW | 18 | 50055 | int32 | Total mains power | 1 W | divide by 1000
20 | Status of the power circuit breakers | register | 45 | 50137 | uint16 | GCB, MCB "is closed" status | - | map bits
21 | Alarm classe class 1, 2, 3 | register | 35 | 50105 | uint16 | Class A, B, C, D, E, F | - | map bits | Class A and B mapped to 1, C and D to 2, E and F to 3
22 | Internal alarms 1 | register | 24, 25, 33 | 50072, 50075, 50102 | uint16 |  | - | map bits | Refer to Alarm mapping sheet
23 | Internal alarms 2 | register | 24, 26 | 50072, 50078. 50216 | uint16 |  | - | map bits | Refer to Alarm mapping sheet
24 | Internal alarms 3 | register | 22, 27 | 50081, 50075, 50066 | uint16 |  | - | map bits | Refer to Alarm mapping sheet
25 | Internal alarms 4 | register | 72 | 50216 | uint16 |  | - | map bits | Refer to Alarm mapping sheet
26 | Displacement voltage | V | 64 | 50193 | int16 | Free AnalogManager Value 3 | - | 1:1 | Use AnalogManager
27 | Operation mode | register | 6 | 50018 | uint16 | Internal flag 1, internal flag 2 | - | map bits | Release GCB = 96.01 Internal flag 1, Changeover setvalue 1/2 = 96.02 Internal flag 2
28 | Running hours hi | h | 42 | 50127 | uint32 | Gen. hours of operation | 0.01 h | divide by 100
29 | Running hours lo | h | 42 | 50127 | uint32 | Gen. hours of operation | 0.01 h | divide by 100
30 | Maintenance call | h | 42 | 50126 | int16 | Hours until next maintenance | 1 h | 1:1
31 | Battery voltage | V x 10 | 7 | 50021 | int16 | Battery voltage | 0.1 V | 1:1
32 | Generator real energy hi | kWh | 40 | 50121 | uint32 | Gen. real energy | 0.01 MWh | multiply by 10
33 | Generator real energy lo | kWh | 40 | 50121 | uint32 | Gen. real energy | 0.01 MWh | multiply by 10
34 | Temperature 1 | °C | 63 | 50191 | int16 | Free AnalogManager Value 1 | - | 1:1 | Use AnalogManager
35 | Temperature 2 | °C | 64 | 50192 | int16 | Free AnalogManager Value 2 | - | 1:1 | Use AnalogManager
36 | Generator re-active energy, positive (lagging) | kvarh | 41 | 50124 | uint32 | Positive reactive generator energy | 0.01 Mvarh | multiply by 10
37 | " low word | kvarh | 41 | 50124 | uint32 | Positive reactive generator energy | 0.01 Mvarh | multiply by 10
38 | Generator re-active energy, negative (leading) | kvarh | 73 | 50219 | int32 | Generator negative reactive energy | 0.01 Mvarh | set to 0
39 | " low word | kvarh | 73 | 50219 | int32 | Generator negative reactive energy | 0.01 Mvarh | set to 0
40 | Generator re-active power | kvar | 19 | 50058 | int32 | Total gen. reactive power | 1 var | divide by 1000

## Alarm mapping
Alarm Bits Mapping for ESEPRO MFR 2 Emulation using Easygen-3000XT
Version 3, 29/08/2024
MFR2 Alarm name | Mux | Easygen-3000XT Alarm name | Comment
Generator overfrequency | 24 | 06.01 Generator over frequency 1 latched OR 06.02 Generator over frequency 2 latched
Generator underfrequency | 24 | 06.03 Generator under frequency OR 06.04 Generator under frequency 2 latched
Generator overvoltage | 24 | 06.05 Generator over voltage 1 latched OR 06.06 Generator over voltage 2 latched
Generator undervoltage | 24 | 06.07 Generator under voltage 1 latched OR 06.08 Generator under voltage 2 latched
Generator overload | 24, 25 | 06.14 Generator overload IOP 1 latched OR 06.15 Generator overload IOP 2 latched OR 06.23 Generator overload MOP 1 latchedd OR 06.24 Generator overload MOP 2 latched
Generator reverse power | 24 | 06.12 Reverse / reduced power 1 latched OR 06.13 Reverse / reduced power 2 latched
Battery undervoltage | 34 | 08.04 Battery under voltage 2 latched OR 08.03 Battery under voltage 1 latched
Generator unbalanced load | 25 | 06.16 Generator unbalanced load 1 latched OR 06.17 Generator unbalanced load 2 latched
Generator overcurrent 1 | 24 | 06.09 Generator over current 1 latched
Generator overcurrent 2 | 24 | 06.10 Generator over current 2 latched OR 06.11 Generator over current 3 latched
Mains overfrequency | 26 | 07.06 Mains over frequency 1 latched OR 07.07 Mains over frequency 2 latched
Mains underfrequency | 26 | 07.08 Mains under frequency 1 latched OR 07.09 Mains under frequency 2 latched
Mains overvoltage | 26 | 07.10 Mains over voltage 1 latched OR 07.11 Mains over voltage 2 latched
Mains undervoltage | 26 | 07.12 Mains under voltage 1 latched OR 07.13 Mains under voltage 2 latched
Mains asymmetry | 72 | 16.01 Free alarm 1 latched | Use LogicManager
Mains phase shift | 26 | 07.14 Mains Phase shift latched
Time monitoring Synchronization | 22 | 08.30 Timeout Synchronisation GCB latched OR 08.31 Timeout Synchronisation MCB latched
df/dt | 27 | 07.15 Mains df/dt latched
Re-active power monitoring lagging | 25 | 06.25 Gen.Power Factor lagging 1 latched OR 06.26 Gen.Power Factor lagging 2 latched OR 07.17 Mains PF lagging 1 latched OR 07.18 Mains PF lagging 2 latched
Re-active power monitoring leading | 25 | 06.27 Gen.Power Factor leading 1 latched OR 06.28 Gen.Power Factor leading 2 latched OR 07.19 Mains PF leading 1 latched OR 07.20 Mains PF leading 2 latched
Displacement voltage | 72 | 16.02 Free alarm 2 latched | Use LogicManager
Temperature monitoring temperature 1 warning | 72 | 16.03 Free alarm 3 latched | Use LogicManager
Temperature monitoring temperature 1 shutdown | 72 | 16.04 Free alarm 4 latched | Use LogicManager
Temperature monitoring temperature 2 warning | 72 | 16.05 Free alarm 5 latched | Use LogicManager
Temperature monitoring temperature 2 shutdown | 72 | 16.06 Free alarm 6 latched | Use LogicManager
Interface alarm |  | n/a | Interface watchdog function not available
Generator PTC (Protocol 409) | 72 | 16.07 Free alarm 7 latched | Use LogicManager
Limiting performance reached (Protocol 408) |  | 16.08 Free alarm 8 latched | Use LogicManager
Generator overtemperature (Protocol 408) |  | 16.09 Free alarm 9 latched | Use LogicManager
Real power surge, positive (Protocol 408) |  | 16.10 Free alarm 10 latched | Use LogicManager
Real power surge, negative (Protocol 408) |  | 16.11 Free alarm 11 latched | Use LogicManager